UNIVERSITÉ DU 20 AOÛT 1955 — SKIKDA

Master — Industrial Automation & Process Control

─────────────────────────────────────

CIP Industrial Automation of CIP Boiler Descaling CODESYS V3.5 SP22 · IEC 61131-3 · ISA-88 · ISA-18.2

Author: Hibatarrahmane boudjelele

# Table of Contents

Table of Contents	2

Executive Summary	4

1.  Introduction	5

1.1  Industrial Context	5

1.2  Project Objectives	5

1.3  Experimental Basis	5

2.  CIP Process Description	6

2.1  Clean-In-Place	6

2.2  Cleaning Sequence	6

3.  System Architecture	7

3.1  Hardware Configuration (SoftPLC)	7

3.2  Software Structure	7

4.  ISA-88 State Machine (FB_CIP)	9

4.1  Procedure State Architecture	9

4.2  State Transition Table	9

4.3  Permissive Evaluation	9

5.  PID Temperature Control (FB_PID_Industrial)	11

5.1  Control Algorithm	11

5.2  Algorithm Features	11

5.3  Initial Tuning Parameters	11

6.  Safety Architecture (FB_SafetyManager)	12

6.1  Execution	12

6.2  Safety Interlocks	12

6.3  Fail-Safe Output States	12

7.  I/O Architecture	13

7.1  Complete I/O Table	13

8.  HMI / Visualization (CIP_HMI)	15

8.1  Design Philosophy	15

8.2  HMI Element Reference	15

9.  Function Block Technical Reference	16

FB_SensorDiag — Analog Input Scaling and Diagnostics	16

FB_SafetyManager — Safety Interlock Execution	16

FB_PID_Industrial — Industrial PID Controller	16

FB_CIP — ISA-88 Procedure State Machine	16

FB_RecipeManager — Recipe Selection and Parameter Loading	16

10.  Teacher's Guide — Opening and Running HIBACIP	18

10.1  Prerequisites	18

10.2  Step 1 — Start CODESYS and Open the Project	18

10.3  Step 2 — Start the SoftPLC Runtime	18

10.4  Step 3 — Connect and Download	18

10.5  Step 4 — Open the Surveillance (Watch Window)	18

10.6  Step 5 — Start the CIP Cycle	19

10.7  Step 6 — Open the HMI Screen	19

10.8  Step 7 — Safety Interlock Demonstration	19

12.  Industrial Commissioning Checklist	20

12.1  Software Pre-Commissioning (FAT)	20

12.2  Site Commissioning (SAT)	20

12.3  PID On-Site Tuning Procedure	20

13.  Cause & Effect Matrix and Alarm List	21

13.1  Cause & Effect Matrix	21

13.2  Alarm Reference List	21

14.  Results and Validation	22

14.1  Simulation Results	22

14.2  Expected Industrial Performance	22

15.  Conclusion	24

References	24

Appendix A — CODESYS Project File Structure	25

A.1  GVL_Setpoints — Tunable Parameters	25

Appendix B — Simulation Quick-Start Values	26

# Executive Summary

The system implements a 15-state ISA-88 compliant procedure state machine that automates a two-phase chemical descaling sequence: an alkaline wash with NaOH 2% at 30°C achieving a mean efficiency of 94.71%, followed by an acetic acid wash at 1% concentration and 40°C achieving 99.60% efficiency. A mandatory intermediate rinse between phases prevents the exothermic reaction that would result from direct contact between the two chemicals.

The HIBACIP platform comprises eight reusable IEC 61131-3 function blocks, four global variable lists, a PID temperature controller with back-calculation anti-windup, three independent safety interlocks (over-temperature, low-flow, overpressure), sensor diagnostics with wire-break detection and IIR filtering, a recipe management system supporting four cleaning protocols, and an ISA-18.2 compliant alarm manager. An interactive HMI visualization (CIP_HMI) provides real-time process overview, operator control, and equipment status display.

| Metric | Value | Standard / Source |
| --- | --- | --- |
| Alkaline wash efficiency | η = 94.71 % | Exp. 07 — NaOH 2%, 30°C |
| Acid wash efficiency | η = 99.60 % | Exp. 21 — CH₃COOH 1%, 40°C |
| Total cycle duration | ≈ 80 minutes | Standard CIP protocol |
| Safety interlocks | 3 (Temp / Flow / Pressure) | IEC 61131-3 / ISA-84 |
| State machine states | 15 (ISA-88 compliant) | ANSI/ISA-88.01 |
| PLC scan cycle | 20 ms (MainTask) | CODESYS IEC-Tasks |
| Conductivity quality gate | ≤ 0.5 mS/cm | NEP rinse protocol |

# 1.  Introduction

## 1.1  Industrial Context

Industrial boilers used in petrochemical refineries are subject to progressive scale deposition from hard water. Calcium carbonate (CaCO₃) deposits on heat-transfer surfaces reduce thermal efficiency by 5 to 10% per millimetre of scale thickness, increase fuel consumption, and can cause localised overheating leading to tube failure. The Skikda Refinery operates a Hot Oil Heater (unit reference 1120-F-1) that requires periodic descaling to maintain operational efficiency.

Traditional descaling methods involve boiler isolation, manual chemical injection, and personnel exposure to corrosive agents, creating both safety and operational downtime risks. An automated CIP (Clean-In-Place) system eliminates manual intervention, ensures consistent chemical concentrations and temperatures, and enforces mandatory safety interlocks that prevent cross-contamination between incompatible chemicals.

## 1.2  Project Objectives

- Design and implement a complete ISA-88 CIP automation sequence for boiler descaling in CODESYS V3.5 SP22

- Integrate PID temperature control for the steam heating circuit with industrial anti-windup protection

- Implement three independent safety interlocks compliant with IEC 61131-3 fail-safe principles

- Create an operator HMI with real-time process visualisation, alarm display, and command interface

- Develop a Python digital twin for hardware-in-the-loop simulation and offline validation

- Provide a complete commissioning and deployment guide for industrial handover

## 1.3  Experimental Basis

The chemical parameters implemented in HIBACIP are derived directly from the systematic experimental work of Boumeghiti & Bekkouche (2021) conducted at Université du 20 Août 1955, Skikda. Their 21-experiment factorial design evaluated NaOH and acetic acid concentration, temperature, and contact time on CaCO₃ removal efficiency. Experiment 07 established the optimal alkaline phase (NaOH 2%, 30°C, 42 min, η = 94.71%) and Experiment 21 the optimal acid phase (CH₃COOH 1%, 40°C, 27 min, η = 99.60%). Acetic acid was selected over hydrochloric acid on the basis of corrosion compatibility with C1020 carbon steel, lower cost, and reduced environmental hazard.

# 2.  CIP Process Description

## 2.1  Clean-In-Place

Clean-In-Place is a methodology for cleaning process equipment interiors without disassembly. For boiler descaling, a recirculating chemical solution is pumped through the boiler's water-side circuit. The sequential application of an alkaline agent followed by an acid dissolves and removes both organic fouling (oils, grease from combustion) and inorganic scale (CaCO₃, calcium silicates). The intermediate rinse between phases is safety-critical: NaOH and acetic acid react exothermically (NaOH + CH₃COOH → CH₃COONa + H₂O + ΔQ), and any residual alkali must be fully purged before acid introduction.

## 2.2  Cleaning Sequence

| Phase | Name | Chemical / Condition | Duration | Purpose |
| --- | --- | --- | --- | --- |
| 1 | Initial Rinse | Fresh water + drain open | 3 min | Flush loose deposits; verify pump health |
| 2 | Alkaline Wash | NaOH 2% @ 30°C (steam PID) | 42 min | Saponify oils; prime scale for acid attack |
| 3 | Intermediate Rinse | Fresh water + drain open | 3 min | SAFETY: purge all NaOH before acid |
| 4 | Acid Wash | CH₃COOH 1% @ 40°C (steam PID) | 27 min | Dissolve CaCO₃: CaCO₃ + 2CH₃COOH → Ca(CH₃COO)₂ + H₂O + CO₂ |
| 5 | Final Rinse | Fresh water + conductivity gate | 5 min | Remove all acid; verify ≤ 0.5 mS/cm before return to service |

The total cycle duration is approximately 80 minutes. A recipe management system (FB_RecipeManager) stores four pre-defined protocols: STD-DESCALE (standard), HEAVY-SCALE (extended durations), LIGHT-MAINT (shortened for preventive maintenance), and PHARMA-GRADE (stricter conductivity gate of 0.3 mS/cm). Each recipe can be loaded by the operator from the HMI before starting the cycle.

# 3.  System Architecture

## 3.1  Hardware Configuration (SoftPLC)

HIBACIP is implemented on CODESYS Control Win V3 x64, which provides a software PLC runtime on a standard Windows PC. This configuration eliminates the need for dedicated PLC hardware, enabling deployment and testing in a laboratory environment. In an industrial deployment, the application would be transferred to a supported CODESYS runtime target (e.g., Wago PFC, Beckhoff CX, or Raspberry Pi with CODESYS Runtime).

## 3.2  Software Structure

The application is structured as a hierarchical collection of IEC 61131-3 objects within a single CODESYS Application node. The execution is governed by a cyclic MainTask with a 20 ms period, calling PLC_PRG as the sole top-level program. All inter-module communication uses Global Variable Lists (GVLs) with the qualified_only attribute to enforce explicit namespace resolution.

| Object | Type | Function |
| --- | --- | --- |
| GVL_IO | Global Var List | All physical I/O signals, raw AI counts, scaled PVs, digital outputs, analog outputs |
| GVL_Setpoints | Global Var List (RETAIN) | Tunable parameters: temperatures, durations, PID gains, conductivity gate |
| GVL_Alarms | Global Var List | Alarm flags, CIP state name, phase progress, batch accumulators |
| GVL_HMI | Global Var List | Operator command interface: START/STOP/HOLD/RESET/ABORT commands, PID manual output |
| FB_SensorDiag | Function Block | 4-20mA scaling, wire-break detection, IIR low-pass filtering, rate-of-change alarm |
| FB_SafetyManager | Function Block | Three safety interlocks with latching, manual reset; determines safe-state outputs |
| FB_PID_Industrial | Function Block | ISA parallel PID, back-calculation anti-windup, derivative filter, manual/auto bumpless |
| FB_CIP | Function Block | ISA-88 15-state procedure machine; inner phase machine; HOLD/RESTART/ABORT logic |
| FB_PumpControl | Function Block | Pump start/stop with run-feedback watchdog, overload monitoring, runtime hour counter |
| FB_ValveControl | Function Block | Solenoid valve open/close with EStop fail-state logic (fail-open/fail-close configurable) |
| FB_AlarmManager | Function Block | ISA-18.2 alarm latching on rising edge, operator acknowledgement, shelving with timeout |
| FB_RecipeManager | Function Block | 4-recipe storage, operator load command, parameter output to GVL_Setpoints |
| PLC_PRG | Program (cyclic) | Top-level execution: sensor scaling → safety → permissive → CIP state machine → PID → outputs |

# 4.  ISA-88 State Machine (FB_CIP)

## 4.1  Procedure State Architecture

The CIP sequence is implemented as a hierarchical ISA-88 state machine within FB_CIP. A super-state machine governs the procedure state (IDLE, RUNNING, HOLDING, HELD, RESTARTING, STOPPING, STOPPED, ABORTING, ABORTED) while an inner phase machine, active only in the RUNNING state, manages the five sequential cleaning phases. This two-tier structure exactly mirrors the ISA-88 recipe model and ensures that HOLD/ABORT commands at the procedure level interrupt the inner phase without requiring explicit handling in each phase branch.

## 4.2  State Transition Table

| From State | To State | Transition Condition | Key Action |
| --- | --- | --- | --- |
| IDLE (0) | RUNNING (1) | cmd_Start = TRUE AND b_Permissive_OK = TRUE | Activate Phase 1 (Init Rinse) |
| RUNNING / Phase 1 | Phase 2 | Phase timer elapsed (3 min) | Close drain; open NaOH valve; enable steam |
| RUNNING / Phase 2 | Phase 3 | Phase timer elapsed (42 min) | Close NaOH; open rinse + drain |
| RUNNING / Phase 3 | Phase 4 | Phase timer elapsed (3 min) | Close drain; open acid valve; enable steam |
| RUNNING / Phase 4 | Phase 5 | Phase timer elapsed (27 min) | Close acid; open rinse + drain |
| RUNNING / Phase 5 | COMPLETE (5) | Timer elapsed AND r_Cond_PV ≤ 0.5 mS/cm | All outputs off; set b_Complete = TRUE |
| RUNNING / Phase 5 | ABORTING (20) | Timer elapsed AND r_Cond_PV > 0.5 mS/cm | Chemical carryover fault; open drain |
| Any RUNNING | HOLDING (10) | cmd_Hold = TRUE OR b_Permissive_OK = FALSE | Freeze timer; maintain pump + rinse |
| HELD (11) | RESTARTING (12) | cmd_Restart = TRUE AND b_Permissive_OK = TRUE | 5s stabilisation delay then resume phase |
| Any | ABORTING (20) | cmd_Abort = TRUE | All chemical outputs off; open drain; 30s drain cycle |
| COMPLETE (5) | IDLE (0) | cmd_Reset = TRUE | Reset accumulators; clear alarm flags |

## 4.3  Permissive Evaluation

Before the state machine can transition from IDLE to RUNNING, and before resuming from HELD, all permissive conditions must simultaneously be true. These are evaluated in PLC_PRG every scan cycle before calling FB_CIP:

- GVL_IO.i_FlowSwitch_Min = TRUE (minimum recirculation flow confirmed)

- GVL_IO.i_EStop_NC = TRUE (hardwired emergency stop NC contact intact)

- GVL_IO.i_CircPump_OL = TRUE (motor overload relay not tripped)

- NOT fbSensTemp.b_WireFault (temperature transmitter signal healthy)

- GVL_IO.r_Flow_PV > 0.0 (flowmeter reading positive)

- GVL_IO.r_Temp_PV < (r_Temp_HighTrip - 10.0) (at least 10°C headroom below trip)

# 5.  PID Temperature Control (FB_PID_Industrial)

## 5.1  Control Algorithm

Temperature regulation of the steam heating circuit during wash phases 2 and 4 is performed by FB_PID_Industrial, implementing the ISA standard parallel-form PID algorithm. The control output drives the steam control valve analog output (AO, 0-100% → 4-20 mA). The PID is enabled only when GVL_IO.q_Steam_Enable is TRUE; at all other times the controller resets to bumpless transfer state.

## 5.2  Algorithm Features

| Feature | Implementation Detail |
| --- | --- |
| Parallel PID form | Output = Kp×e + (Kp/Ti)×∫e dt + Kp×Td×de/dt. Each term independently tunable. |
| Anti-windup | Back-calculation method: BackCalc = (Dt/Ti) × (u_clamped - u_raw). Corrects integrator when output saturates, preventing integrator runaway during temperature warm-up phase. |
| Derivative filter | First-order filter on PV (not error): D_filt = (Td×(PV_prev-PV)/Dt + D_filt×Tf)/(Tf+Dt). Applied to process variable to eliminate setpoint-change derivative kick. |
| Bumpless transfer | In manual mode: pre-loads integrator to manual_output value so that switching to auto produces zero output step. |
| Output clamping | Hard clamp 0-100%. Saturation flags b_Saturated_Hi and b_Saturated_Lo inform HMI. |
| Process alarms | Four PV-based alarms: HiHi (55°C default), Hi (45°C), Lo (15°C), LoLo (10°C). Independent of mode. |

## 5.3  Initial Tuning Parameters

Starting tuning values based on approximate estimation for typical small boiler (gain K≈0.8°C/%, time constant τ≈120 s, dead time θ≈5 s) using Lambda tuning with λ=τ/3:

- Kp = 3.5  (proportional gain)

- Ti = 12.5 s  (integral time)

- Td = 6.25 s  (derivative time)

- Tf = 0.5 s   (derivative filter time constant)

- Dt = 0.02 s  (scan period — matches MainTask 20 ms)

These values must be re-tuned on-site using a step-response bump test before commissioning on real hardware.

# 6.  Safety Architecture (FB_SafetyManager)

## 6.1  Execution

Safety evaluation is the first function block called in PLC_PRG every scan cycle, before the CIP state machine, before the PID controller, and before any output is driven. This deterministic ordering guarantees that no hazardous condition can persist for more than one PLC scan cycle (20 ms). If any interlock fires, PLC_PRG immediately drives all outputs to their fail-safe states and returns without executing any other logic.

## 6.2  Safety Interlocks

| IL | Name | Trip Condition | Engineering Rationale |
| --- | --- | --- | --- |
| 1 | High Temperature | r_Temp_PV ≥ 60°C OR AI wire fault | At temperatures above 60°C, acetic acid corrosion rate on C1020 carbon steel accelerates exponentially. Additionally thermal runaway risk from uncontrolled steam valve. Optimal experimental results at 30-40°C confirm 60°C as a safe absolute ceiling. |
| 2 | Low Flow / Pump Fault | Pump commanded AND no run feedback for > 3 s | Without recirculation flow, chemical concentration becomes non-homogeneous. Stagnant pockets of NaOH or acid in tube dead-legs create concentration-cell corrosion pitting. Three-second delay tolerates transient start-up. |
| 3 | Overpressure | r_Pressure_PV ≥ 6.0 bar OR pressure AI wire fault | Normal CIP operating pressure is 1-2 bar. Blocked drain valve, steam valve failure, or closed isolation valve during heat-up could cause rapid pressure rise. Wire-break fault treated as worst-case (maximum pressure) fail-safe. |

## 6.3  Fail-Safe Output States

When any interlock latches, all process outputs are immediately driven to their fail-safe de-energised states:

- q_CircPump = FALSE  (pump stops immediately)

- q_NaOH_Valve = FALSE  (NaOH valve closes — spring-return, fail-closed)

- q_AcAc_Valve = FALSE  (acid valve closes)

- q_Steam_Enable = FALSE  (steam valve disabled — spring closes)

- q_Drain_Valve = TRUE  (drain opens — fail-open for pressure relief)

- r_SteamValve_Pct = 0.0  (analog output driven to 0%)

The EStop latch is retained until the operator performs a manual reset: the hardware key-switch must be set (i_SafetyReset = TRUE) while all underlying fault conditions have cleared. This two-condition reset (fault cleared AND operator action) prevents inadvertent restart.

# 7.  I/O Architecture

## 7.1  Complete I/O Table

| Tag Name | Type | Address | Description | Range | Fail-Safe |
| --- | --- | --- | --- | --- | --- |
| ANALOG INPUTS — 4–20 mA → 0–32767 counts |  |  |  |  |  |
| w_Temp_RawAI | AI | %IW0 | TT-101 PT100 temperature transmitter | 0–100 °C | Wire-break → -999 |
| w_Pres_RawAI | AI | %IW1 | PT-101 pressure transmitter | 0–10 bar | Wire-break → trip |
| w_Flow_RawAI | AI | %IW2 | FT-101 magnetic flowmeter | 0–100 L/min | Wire-break → -999 |
| w_Cond_RawAI | AI | %IW3 | CT-101 conductivity transmitter (quality gate) | 0–20 mS/cm | Wire-break → trip |
| DIGITAL INPUTS |  |  |  |  |  |
| i_Start_Command | DI | %IX0.0 | HMI/panel START pushbutton (NO) | 0/1 | 0 = stop |
| i_EStop_NC | DI | %IX0.1 | Hardwired emergency stop (NC) | 1=OK / 0=Trip | 0 = safe/trip |
| i_CircPump_RunFB | DI | %IX0.2 | Circulation pump contactor auxiliary (NO) | 1 = running | 0 |
| i_CircPump_OL | DI | %IX0.3 | Pump motor overload relay (NC) | 1=OK / 0=Trip | 0 = trip |
| i_FlowSwitch_Min | DI | %IX0.4 | Minimum flow switch (NO, permissive) | 1 = flow OK | 0 = no flow |
| i_SafetyReset | DI | %IX0.5 | Key-switch safety reset (NO) | Pulse 1 = reset | 0 |
| DIGITAL OUTPUTS |  |  |  |  |  |
| q_CircPump | DO | %QX0.0 | Circulation pump contactor coil | 1 = run | 0 = stop |
| q_NaOH_Valve | DO | %QX0.1 | NaOH solenoid valve (fail-closed) | 1 = open | 0 = closed |
| q_AcAc_Valve | DO | %QX0.2 | Acetic acid solenoid valve (fail-closed) | 1 = open | 0 = closed |
| q_Rinse_Valve | DO | %QX0.3 | Rinse water solenoid valve | 1 = open | 0 = closed |
| q_Drain_Valve | DO | %QX0.4 | Drain solenoid valve (fail-OPEN) | 1 = open | 1 = open (safe) |
| q_Steam_Enable | DO | %QX0.5 | Steam valve enable relay (enables PID AO) | 1 = enabled | 0 = disabled |
| ANALOG OUTPUT — 0–100% → 4–20 mA |  |  |  |  |  |
| w_SteamValve_AO | AO | %QW0 | Steam control valve (PID output → modulating) | 0–32767 | 0 = closed |

# 8.  HMI / Visualization (CIP_HMI)

## 8.1  Design Philosophy

The CIP_HMI visualization is built within CODESYS's integrated visualization environment and follows ISA-101 HMI design principles: equipment objects use a consistent colour language (grey = off/normal, green = running, amber = warning state, red = fault/active), process values are displayed in engineering units with context labels, and operator action buttons are visually distinct from status displays.

## 8.2  HMI Element Reference

| # | Element | Variable Linked | Normal State | Active State |
| --- | --- | --- | --- | --- |
| 1 | State Rectangle | GVL_Alarms.s_State_Name | 'IDLE' (grey) | 'RUNNING' etc. |
| 2 | Progress Bar | GVL_Alarms.r_Phase_Progress | 0% | 0 → 100% |
| 3 | Temperature Display | GVL_IO.r_Temp_PV | Live °C value | Red if > Hi limit |
| 4 | Conductivity Display | GVL_IO.r_Cond_PV | Live mS/cm | Yellow if > gate |
| 5 | Flow Display | GVL_IO.r_Flow_PV | Live L/min | Red if < min |
| 6 | START Button (green) | GVL_IO.i_Start_Command (toggle) | Off | Starts CIP cycle |
| 7 | STOP Button (red) | GVL_HMI.b_Stop_Cmd (toggle) | Off | Controlled shutdown |
| 8 | RESET Button (amber) | GVL_HMI.b_Reset_Cmd (toggle) | Off | Returns to IDLE |
| 9 | POMPE Lamp (ellipse) | GVL_IO.q_CircPump | Grey = pump off | Green = pump on |
| 10 | NAOH Lamp | GVL_IO.q_NaOH_Valve | Grey = closed | Amber = open |
| 11 | ACIDE Lamp | GVL_IO.q_AcAc_Valve | Grey = closed | Red = open |
| 12 | RINÇAGE Lamp | GVL_IO.q_Rinse_Valve | Grey = closed | Cyan = open |
| 13 | ALARME Lamp (blinks) | GVL_Alarms.b_EStop_Active | Grey = no alarm | Red blink = EStop |

# 9.  Function Block Technical Reference

## FB_SensorDiag — Analog Input Scaling and Diagnostics

Converts a raw 16-bit AI count (0-32767) to an engineering-unit REAL value using linear interpolation: EU = (Raw/32767) × (EU_Hi - EU_Lo) + EU_Lo. A first-order IIR low-pass filter with configurable coefficient α (default 0.15) smooths measurement noise. Wire-break detection triggers when the raw count falls below the threshold (default 1000 counts ≈ 2 mA on a 4-20 mA circuit). When a wire fault is detected, the output r_FilteredPV is set to the sentinel value -999.0 so that downstream logic can unambiguously detect sensor failure and the safety interlock evaluates conservatively.

## FB_SafetyManager — Safety Interlock Execution

Evaluates three independent interlock conditions every PLC scan. Each active interlock increments an internal counter (n_Count). If n_Count > 0, the latch b_EStop_Active is set and remain set (sticky) until the operator performs a manual reset. The reset gate requires all fault conditions to have cleared AND the key-switch input (b_SafetyReset) to pulse TRUE. This two-condition requirement prevents inadvertent restart after a trip. Safe-state outputs (q_SafeState_Drain = TRUE) are driven by this FB directly.

## FB_PID_Industrial — Industrial PID Controller

Implements the ISA parallel form output equation: u = Kp×e + (Kp/Ti)×∫e dt + Kp×Td×de/dt, with a first-order derivative filter on the process variable (not the error) to prevent setpoint-kick on reference changes. Back-calculation anti-windup is applied when the raw output saturates: the integrator is corrected by (Dt/Ti)×(u_clamped - u_raw). In manual mode, the integrator is pre-loaded to the manual output setpoint so that switching to automatic mode produces a zero-step output transition (bumpless transfer). The controller executes only when b_Auto = TRUE and q_Steam_Enable is asserted.

## FB_CIP — ISA-88 Procedure State Machine

The core control logic. The outer CASE statement dispatches on the procedure state (integer 0-31). Within state 1 (RUNNING), a nested CASE on n_Phase (1-5) manages the individual cleaning phases. Each phase: sets the appropriate valve and pump outputs, configures the active temperature setpoint (r_Temp_SP_Active) for the PID, arms a TON phase timer, and monitors the timer Q output for advancement to the next phase. The ABORT handler has highest priority and is evaluated before the HOLD detection, which in turn is evaluated before the main state dispatch, providing a deterministic priority hierarchy.

## FB_RecipeManager — Recipe Selection and Parameter Loading

Stores four hard-coded cleaning recipes as inline CASE constants. When the operator sets n_SelectRecipe (1-4) and pulses b_Load_Cmd, the corresponding parameters are loaded to the output variables: alkaline temperature, acid temperature, alkaline duration, acid duration, and conductivity gate. These outputs are wired to GVL_Setpoints parameters in PLC_PRG, making them available to FB_CIP and FB_PID_Industrial without cross-referencing.

10.  Teacher's Guide — Opening and Running HIBACIP

## 10.1  Prerequisites

- Software: CODESYS V3.5 SP22 Patch 2 (or newer) installed on a Windows 64-bit PC

- Runtime: CODESYS Control Win V3 x64 installed (included with CODESYS installer)

- Files received: HIBACIP.project  (protect-locked — password provided separately)

- No additional hardware required — all tests run in software simulation mode

## 10.2  Step 1 — Start CODESYS and Open the Project

- Launch CODESYS from the Start menu or Desktop shortcut

- Menu: Fichier (File) → Ouvrir (Open) → Projet (Project)

- Browse to the location of HIBACIP.project → click Open

- If prompted for a password: enter the provided project password → OK

- The project tree on the left panel should show: Application with all GVLs and FBs

## 10.3  Step 2 — Start the SoftPLC Runtime

- Look in the Windows System Tray (bottom right, near the clock)

- Find the CODESYS Control Win V3 icon (gear symbol)

- If not visible: Start menu → search 'CODESYS Control Win V3' → click to start it

- The icon should show a green indicator → the runtime is ready

- If the icon shows red: right-click the icon → Start PLC

## 10.4  Step 3 — Connect and Download

- In CODESYS menu: En ligne (Online) → Se connecter (Connect)

- Select 'CODESYS Control Win V3 x64' in the device list → OK

- Press Ctrl+L (Connexion / Login) — this compiles and downloads the code

- If asked 'Download to device?': click Oui (Yes)

- Press F5 (Démarrer / Start) — the PLC begins cyclic execution

- Confirm: bottom status bar shows 'EXÉCUTION' in green

## 10.5  Step 4 — Open the Surveillance (Watch Window)

- Menu: Affichage (View) → Fenêtres de débogage → Surveillance 1

- In the Expression column, add these variables (click empty row, type, press Enter):

- GVL_Alarms.s_State_Name  — shows current CIP state (initially 'IDLE')

- GVL_IO.r_Temp_PV  — live temperature reading

- PLC_PRG.fbSafety.b_EStop_Active  — must be FALSE before starting

- PLC_PRG.b_Permissive_OK  — must be TRUE before CIP will start

- GVL_Alarms.r_Phase_Progress  — phase completion percentage

## 10.6  Step 5 — Start the CIP Cycle

- In the Surveillance, find GVL_IO.i_Start_Command

- Click in the 'Valeur préparée' column next to it

- Type: TRUE → press Enter → press Ctrl+F7 to write

- Observe: GVL_Alarms.s_State_Name changes from 'IDLE' to 'RUNNING'

- Observe: GVL_IO.q_CircPump becomes TRUE (pump starts)

- Observe: GVL_IO.q_Rinse_Valve becomes TRUE (Phase 1: Initial Rinse)

- The progress bar in CIP_HMI begins filling from 0% to 100%

## 10.7  Step 6 — Open the HMI Screen

- In the left project tree: double-click CIP_HMI

- The visualization opens in a separate floating window

- All lamps, values, and buttons operate in real time

- The POMPE lamp turns green when the pump runs

- The ALARME lamp remains grey when no safety fault is active

- Click the STOP button at any time for a controlled 30-second flush then stop

- Click RESET to return to IDLE state ready for the next cycle

## 10.8  Step 7 — Safety Interlock Demonstration

To demonstrate the over-temperature interlock to the audience:

- While the CIP is RUNNING, in the Surveillance window:

- Set GVL_IO.w_Temp_RawAI = 20000 (→ simulates ≈ 61°C, above the 60°C trip)

- Press Ctrl+F7 to write

- Observe immediately: PLC_PRG.fbSafety.b_EStop_Active = TRUE

- Observe: all pump and valve outputs drop to FALSE

- Observe: q_Drain_Valve = TRUE (drain opens for safety venting)

- Observe: ALARME lamp on HMI turns red and blinks

To reset after the demonstration: set w_Temp_RawAI = 7209 (22°C) → Ctrl+F7, then set i_SafetyReset = TRUE → Ctrl+F7 → then i_SafetyReset = FALSE → Ctrl+F7.

# 11.  Industrial Commissioning Checklist

## 11.1  Software Pre-Commissioning (FAT)

- Compile project: F11 → confirm 0 errors, 0 warnings

- Simulate all 5 CIP phases in SoftPLC mode using reduced durations

- Test HOLD/RESTART across each phase; verify timer resumes from correct position

- Test ABORT from each phase; verify drain opens and 30-second drain cycle completes

- Force all three interlocks in sequence; verify safe-state outputs in each case

- Verify alarm acknowledgement and shelving logic in FB_AlarmManager

- Load all four recipes and confirm parameter changes in GVL_Setpoints

- Test PID step response in manual/auto bumpless transfer

- Verify OPC UA tag browsing from UaExpert client

- Sign FAT protocol with customer witness signature

## 11.2  Site Commissioning (SAT)

- Physical I/O loop check: each of 12 DI, 6 DO, 4 AI, 1 AO verified at field instrument

- Emergency stop circuit continuity verified (NC contact chain)

- Circulation pump start/stop: run feedback timing < 3 seconds

- Valve stroking: all solenoids confirmed open/close within travel timeout

- Temperature probe wet calibration: ice bath (0°C) and steam comparison (≈100°C)

- Conductivity sensor wet calibration: reference buffer solutions at 0.5 mS/cm and 8 mS/cm

- Flowmeter zeroing: confirmed zero flow reading with pump stopped

- PID bump test on actual steam valve and boiler thermal mass

- First wet CIP run with clean water only (no chemical): verify all transitions

- First chemical CIP run under observation: document temperatures, conductivity, phase durations

- Conductivity gate test: verify system aborts when final rinse conductivity remains above 0.5 mS/cm

- Sign SAT protocol: handover to operations team

## 11.3  PID On-Site Tuning Procedure

- Set PID to manual: set b_Auto = FALSE, r_Manual_Out = 30.0 in Surveillance

- Wait for temperature to stabilise (drift < 0.1°C/min)

- Apply 10% output step: change r_Manual_Out from 30.0 to 40.0

- Record temperature response every 10 seconds until new steady state

- From the step response, identify: K = ΔT/ΔOutput, τ = 63% response time, θ = dead time

- Calculate Lambda tuning: Kp = τ/(K×(τ/3 + θ)), Ti = τ, Td = θ/2

- Enter calculated values in Surveillance: GVL_Setpoints.r_PID_Kp, r_PID_Ti, r_PID_Td

- Switch to auto, apply setpoint step, verify < 5% overshoot, < 2 oscillations

# 12.  Cause & Effect Matrix and Alarm List

## 12.1  Cause & Effect Matrix

| Cause | Pump | NaOH V. | Acid V. | Steam | Drain | State | Alarm | Priority |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| High temperature ≥ 60°C | STOP | CLOSE | CLOSE | OFF | OPEN | ABORT | A1 | CRITICAL |
| Overpressure ≥ 6 bar | STOP | CLOSE | CLOSE | OFF | OPEN | ABORT | A1 | CRITICAL |
| Pump run FB lost (3 s) | — | CLOSE | CLOSE | OFF | — | HOLD | A2 | HIGH |
| E-Stop button pressed | STOP | CLOSE | CLOSE | OFF | OPEN | ABORT | A1 | CRITICAL |
| Temp AI wire break | — | CLOSE | CLOSE | OFF | — | HOLD | A2 | HIGH |
| Final rinse cond. fail | — | — | — | — | OPEN | ABORT | A2 | HIGH |

## 12.2  Alarm Reference List

| Tag | Priority | Description | Reset Method |
| --- | --- | --- | --- |
| b_Alarm_HighTemp | 1 — Critical | Process temperature at or above 60°C safety trip | Auto-clear when temp < trip; key-switch + HMI reset |
| b_Alarm_HighPres | 1 — Critical | Process pressure at or above 6.0 bar | Auto-clear when pressure < trip; key-switch + HMI reset |
| b_Alarm_PumpFault | 2 — High | Pump commanded ON but run feedback not received within 3 seconds | Clear fault; key-switch + HMI reset |
| b_Alarm_RinseFail | 2 — High | Final rinse conductivity > 0.5 mS/cm at end of rinse timer — chemical carryover | Investigate chemical residue; manual operator reset after extended rinse |
| b_Alarm_AI_Fault | 2 — High | Temperature or pressure AI signal below wire-break threshold (< 2 mA equivalent) | Check instrument and wiring; auto-clears when signal restored |

# 13.  Results and Validation

## 13.1  Simulation Results

| Test | Expected Result | Outcome |
| --- | --- | --- |
| Full 5-phase cycle (reduced durations) | COMPLETE state, b_CIP_Complete = TRUE | PASSED — all 5 phases executed in correct sequence |
| HOLD during Phase 2 (alkaline wash) | State: HELD; timer frozen; pump + rinse maintained | PASSED — phase resumed from correct position on RESTART |
| ABORT from Phase 4 (acid wash) | State: ABORTING; drain opens; 30 s drain cycle | PASSED — drain opened immediately; ABORTED after 30 s |
| Interlock 1: Temperature ≥ 60°C | All outputs off; drain open; EStop latched | PASSED — response within one PLC scan (20 ms) |
| Interlock 2: Pump run feedback lost | EStop after 3 s; chemical valves closed | PASSED — pump fault alarm raised at 3.02 s |
| Interlock 3: Pressure ≥ 6 bar | All outputs off; drain open; EStop latched | PASSED — trip fired immediately on threshold crossing |
| Conductivity gate FAIL (cond > 0.5 mS/cm) | ABORT triggered; b_Alarm_RinseFail = TRUE | PASSED — alarm raised; ABORTING state entered |
| Safety reset procedure | EStop clears only when all faults cleared AND key-switch pulsed | PASSED — premature reset attempt without fault clearance rejected |
| PID temperature control (simulation) | Temperature tracks setpoint with < 10% overshoot | PASSED — simulated rise to 30°C SP with stable oscillation-free response |
| All 4 recipes loaded and validated | Correct durations and temperatures applied to state machine | PASSED — PHARMA-GRADE recipe verified with 0.3 mS/cm conductivity gate |

## 13.2  Expected Industrial Performance

the optimal HIBACIP cleaning protocol (Recipe 1: STD-DESCALE) is expected to achieve:

- CaCO₃ removal efficiency: 94.71% (alkaline phase) → 99.60% (acid phase combined)

- Total chemical consumption: approximately 50 L NaOH solution + 25 L acetic acid solution per cycle

- Energy consumption: estimated 2-4 kWh steam heating per cycle depending on starting temperature

- Boiler thermal efficiency recovery: 5-10 percentage points per 1 mm scale thickness removed

# 14.  Conclusion

This project successfully delivers a complete, industrial-grade automated CIP boiler descaling control system named HIBACIP, implemented in CODESYS V3.5 SP22 using IEC 61131-3 Structured Text. The system achieves all stated objectives: an ISA-88 compliant state machine managing a validated two-phase chemical sequence, industrial PID temperature control with anti-windup protection, three independent safety interlocks enforcing fail-safe behaviour, a fully functional operator HMI.

The HIBACIP architecture demonstrates industrial automation best practices throughout: deterministic safety-first execution ordering, qualified global variable namespaces, reusable function block design, bumpless PID transfer, wire-break sensor diagnostics, ISA-18.2 alarm management, and recipe-driven operation. The underlying chemical parameters are grounded in systematic experimental research specific to carbon-steel boiler systems in the petrochemical environment of Skikda.

## References

- Boumeghiti A., Bekkouche B. (2021). Étude expérimentale du détartrage chimique des chaudières industrielles. Mémoire de Master, Université du 20 Août 1955 — Skikda.

- IEC 61131-3:2013. Programmable controllers — Part 3: Programming languages. International Electrotechnical Commission.

- ANSI/ISA-88.01-1995. Batch Control — Part 1: Models and Terminology. International Society of Automation.

- ANSI/ISA-18.2-2016. Management of Alarm Systems for the Process Industries.

- 3S-Smart Software Solutions GmbH. CODESYS V3.5 SP22 — Complete Online Help. Kempten, Germany, 2024.

- Seborg D.E., Edgar T.F., Mellichamp D.A., Doyle F.J. (2016). Process Dynamics and Control, 4th ed. Wiley.

# Appendix A — CODESYS Project File Structure

## A.1  GVL_Setpoints — Tunable Parameters

| r_Alk_Temp_SP | 30.0 | °C | NaOH phase temperature setpoint (PID target during Phase 2) |
| --- | --- | --- | --- |
| r_Acid_Temp_SP | 40.0 | °C | Acid phase temperature setpoint (PID target during Phase 4) |
| r_Temp_HighTrip | 60.0 | °C | Interlock 1 trip setpoint — do not exceed without engineering review |
| r_Cond_Baseline | 0.5 | mS/cm | Final rinse quality gate — system aborts if exceeded after full rinse duration |
| r_Dur_InitRinse | 180.0 | s | Phase 1 Initial Rinse duration (default 3 min) |
| r_Dur_AlkWash | 2520.0 | s | Phase 2 Alkaline Wash duration (default 42 min — Exp.07 optimum) |
| r_Dur_InterRinse | 180.0 | s | Phase 3 Intermediate Rinse — must not be shortened below 120 s |
| r_Dur_AcidWash | 1620.0 | s | Phase 4 Acid Wash duration (default 27 min — Exp.21 optimum) |
| r_Dur_FinalRinse | 300.0 | s | Phase 5 Final Rinse before conductivity gate evaluation |
| r_PID_Kp | 3.5 | — | PID proportional gain — adjust after on-site bump test |
| r_PID_Ti | 12.5 | s | PID integral time — increase to reduce overshoot |
| r_PID_Td | 6.25 | s | PID derivative time — set to 0 if noisy sensor reading |

GVL_Setpoints uses the VAR_GLOBAL RETAIN declaration. This means all setpoint values survive a warm power cycle (PLC power off/on) and retain the last operator-written values. A cold reset (power cycle with CODESYS Control Win service stopped) reloads the compiled defaults listed above.

# Appendix B — Simulation Quick-Start Values

Use these values in the CODESYS Surveillance window (Ctrl+F7 to write) to enable simulation without physical hardware:

| Variable | Sim Value | Represents |
| --- | --- | --- |
| GVL_IO.w_Temp_RawAI | 7209 | 22°C ambient temperature |
| GVL_IO.w_Flow_RawAI | 8192 | 25 L/min recirculation flow |
| GVL_IO.w_Cond_RawAI | 1311 | 0.8 mS/cm (initial scaled water) |
| GVL_IO.w_Pres_RawAI | 6554 | 2 bar operating pressure |
| GVL_IO.i_EStop_NC | TRUE | Emergency stop NOT pressed (NC contact healthy) |
| GVL_IO.i_FlowSwitch_Min | TRUE | Minimum flow confirmed |
| GVL_IO.i_CircPump_OL | TRUE | Motor overload relay not tripped |
| GVL_Setpoints.r_Dur_InitRinse | 10.0 | 10-second rinse (for fast demo — reset to 180 for real operation) |